## Phasing Plan
| 656-18-300 | SPS HVAC and Environmental Controls
Working Hours
Phase | Phase Length | Building | AHU # | Type | SPS Room Name, Number | Room Square footage | Maximum SPS Room Impact Length* | AHU Location | The below working hours are focused on mitigating impacts to provided care in occupied spaces. The hours are generic in nature and are a guide. Each location, being unique in design may require additional off-hours work prior to work inside the SPS room and after work inside the SPS room. This work shall be coordinated with the COR to minimize impacts to provided care.
0 | 21 Calendar Days | 48 | N/A |  | #108, #106C | 200, 200 | N/A | N/A | Day Hours (8:00 AM-4:30 PM) ); Convert two rooms into SPS, clean supplies LMS directive compliant with positive pressure, removing plumbing, 1 hr. rated fire walls, doors. See attachment for Phase 0.
1 | 21 Calendar Days | 111 | 111-AHU-25 | Horizontal Split | SPS #25 | 60 | 10 Calendar Days | Crawl Space | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
2 | 21 Calendar Days | 50 | 50-AHU-229 | Horizontal Split | Storage #229 | 232 | 10 Calendar Days | NW Attic | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
3 | 21 Calendar Days | 28 | 28-AHU-210 | Horizontal Split | SPS #210 | 36 | 10 Calendar Days | West Attic | Day Hours (8:00 AM-4:30 PM)
|  | 50 | 50-AHU-291 | Horizontal Split | Clean Utility #291 | 50 | 10 Calendar Days | East Attic | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
4 | 21 Calendar Days | 28 | 28-AHU-257 | Vertical Split | SPS #257 | 28 | 10 Calendar Days | East Attic | Day Hours (8:00 AM-4:30 PM)
|  | 116 | 116-AHU-106 | Horizontal Split | Clean Utility #106 | 56 | 10 Calendar Days | Crawl Space #002 | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
5 | 21 Calendar Days | 2 | 2-AHU-117 | Packaged | Storage #117 | 48 | 10 Calendar Days | Outside Grade | Day Hours (8:00 AM-4:30 PM)
|  | 51 | 51-AHU-160 | Vertical Split | Supply Storage #160 | 28 | 10 Calendar Days | Basement Clean Linen Room #18 | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
6 | 21Calendar Days | 3 | 3-AHU-113 | Packaged | Clean SPS #113 | 120 | 10 Calendar Days | Outside Grade | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
7 | 21 Calendar Days | 49 | 49-AHU-14 | Vertical Split | SPS #14 | 50 | 10 Calendar Days | Basement Office #14B | Day Hours (8:00 AM-4:30 PM)
|  | 29 | 29-AHU-7 | Vertical Split | SPS Storage #7 | 90 | 10 Calendar Days | Basement Low Voltage Room CO2A | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
8 | 21 Calendar Days | 49 | 49-AHU-130 | Horizontal Split | Clean Utility #130 | 80 | 10 Calendar Days | Basement Mech Room #7 | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
9 | 21 Calendar Days | 29 | 29-AHU-146 | Horizontal Split | Clean/SPD #146 | 48 | 10 Calendar Days | Patient Encounter #148 | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
10 | 21 Calendar Days | 49 | 49-AHU-230 | Horizontal Split | Clean Utility #230 | 80 | 10 Calendar Days | NW Attic | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
11 | 21 Calendar Days | 51 | 51-AHU-244 | Horizontal Split | SPD Supply #244 | 56 | 10 Calendar Days | West Attic | Day Hours (8:00 AM-4:30 PM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
12 | 21 Calendar Days | 1 | 1-AHU-51 | Horizontal Split | Clean Linen #51 | 100 | 10 Calendar Days | Basement Crawl Space | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
13 | 21 Calendar Days | 1 | 1-AHU-208 | Vertical Split | Clean #208 | 72 | 2.4 Calendar Days | East Attic | Off-Hours * Special Hours: Work in SPS room to start on a Friday at 6:00 PM and continue for 58 straight hours until 4:00 AM Monday morning. Work in the SPS room must be completed by 4:00 AM Monday morning.
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
14 | 21 Calendar Days | 1 | 1-AHU-232 | Horizontal Split | Scope Room #232 | 48 | 10 Calendar Days | West Attic | Off-Hours (5:30 PM-2:00 AM)
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
15 | 21 Calendar Days | 1 | 1-AHU-248 | Horizontal Split | Storage #248 | 200 | 2.4 Calendar Days | West Attic | Off-Hours * Special Hours: Work in SPS room to start on a Friday at 6:00 PM and continue for 58 straight hours until 4:00 AM Monday morning. Work in the SPS room must be completed by 4:00 AM Monday morning.
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
16 | 21 Calendar Days | 1 | 1-AHU-111C | Horizontal Split | Supply Equipment #111C | 144 | 10 Calendar Days | Corridor C1ED | Off-Hours * Special Hours (6:30 PM - 4:00 AM) Daily, ceiling will have to be restored each morning in corridor C1ED prior to urgent care opening up.
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
17 | 17 Calendar Days | 1 | 1-AHU-160A | Horizontal Split | Clean Utility #160A | 39 | 4 Calendar Days | Corridor C1WJ | Off-Hours * Special Hours: Work in SPS room to start on a Friday at 6:00 PM and continue for 58 straight hours until 4:30 AM Monday morning. Work in the SPS room must be completed by 4:00 AM Monday morning.
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
18 | 17 Calendar Days | 1 | 1-AHU-A217 | Packaged | Sterile Supplies #A217 | 561 | 3.33 Calendar Days | 1st Floor Roof | Off-Hours * Special Hours: Work in the SPS room to start on a Thursday at 8:00 PM and continue for 80 hours until the following Monday morning at 4:00 AM. Work must be completed by 4:00 AM Monday.
| 3 Business Days | [7 empty] | VA SPS and Logistics Supplies Relocation Corrdination
19 | 21 Calendar Days | 48 | N/A |  | #108, #106C | 200, 200 | N/A | N/A | Day Hours (8:00 AM-4:30 PM) ); Restore rooms patient rooms. Restore plumbing, fire wall rated materials and pressures to patient room standards.

## Impact Types
Building | Level | Room # | Description | Demo or New
1 | Basement | A-10 | Crawl Space | New
1 | Basement | 50 | Office | New
1 | Basement | CO-H3 | Corridor | New
1 | Basement | 51 | Clean Linen | New
1 | Basement | 50 | Office | Demo
1 | Basement | 51 | Clean Linen | Demo
1 | 1st Floor | 111C | Supply Equipment | Demo
1 | 1st Floor | 111D | Multipurpose | Demo
1 | 1st Floor | 111C | Supply Equipment | New
1 | 1st Floor | 111D | Multipurpose | New
1 | 1st Floor | 160A | Clean Utility | Demo
1 | 1st Floor | 160 | Special Procedure Storage | Demo
1 | 1st Floor | 160A | Clean Utility | New
1 | 1st Floor | 160 | Special Procedure Storage | New
1 | 1st Floor | C1WH | Corridor | New
1 | 2nd Floor | 208 | Clean | Demo
1 | 2nd Floor | C23A | Corridor | Demo
1 | 2nd Floor | 208 | Clean | New
1 | 2nd Floor | C23A | Corridor | New
1 | 2nd Floor | A217 | Sterile Supplies | Demo
1 | 2nd Floor | C2-A4 | Hall | Demo
1 | 2nd Floor | C2-A3 | Hall | Demo
1 | 2nd Floor | A217 | Sterile Supplies | New
1 | 2nd Floor | C2-A4 | Hall | New
1 | 2nd Floor | C2-A3 | Hall | New
1 | 2nd Floor | Roof | 1st Floor Roof | New
1 | 2nd Floor | 232 | Scope Room | Demo
1 | 2nd Floor | C2W | Corridor | Demo
1 | 2nd Floor | 232 | Scope Room | New
1 | 2nd Floor | C2W | Corridor | New
1 | 2nd Floor | 237 | Recovery | New
1 | 2nd Floor | 248 | Storage | Demo
1 | 2nd Floor | C2WC | Corridor | Demo
1 | 2nd Floor | 248 | Storage | New
1 | 2nd Floor | C2WC | Corridor | New
1 | 2nd Floor | C2WB | Corridor | New
1 | 3rd Floor | Attic | Attic Space | New
1 | 1st Floor | Roof | Roof | Piping
1 | 1st Floor | 152 | Nurse/Chart | Piping
1 | 1st Floor | 152A | Med | Piping
1 | 1st Floor | 153 | Initial Exam | Piping
1 | 1st Floor | C1WF | Corridor | Piping
1 | 1st Floor | C1WG | Corridor | Piping
1 | 1st Floor | 160 | Special Procedure | Piping
1 | 1st Floor | 122 | MMA | Piping
1 | 1st Floor | Roof | Basement | Piping
1 | 1st Floor | 120 | Waiting | Piping
1 | 1st Floor | C1EA | Corridor | Piping
1 | 1st Floor | 113 | Nourishment | Piping
1 | 1st Floor | 111C | Supply Equipment | Piping
1 | 1st Floor | C1ED | Corridor | Piping
1 | 2nd Floor | C2WC | Corridor | Piping
1 | 2nd Floor | 241 | Soiled Utility | Piping
1 | 2nd Floor | 243A | HAC | Piping
1 | 2nd Floor | A217 | Sterile Supplies | Piping
1 | 2nd Floor | 214 | Storage | Piping
1 | 2nd Floor | 217 | HAC | Piping
1 | Attic | Attic | Attic Space | Piping
2 | 1st Floor |  | Outside | Demo
2 | 1st Floor |  | Outside | New
2 | 1st Floor | 117 | Storage | New
2 | 1st Floor | C1E | Corridor | New
2 | Basement |  | Steam Tunnel | New
2 | Basement | 11 | Mechanical Room | New
2 | Basement | COE | Corridor | New
2 | Basement | 1 | HAC | New
2 | Basement |  | Unexcavated Area | New
2 | 1st Floor | C1E | Corridor | New
2 | Basement |  | Unexcavated Area | New
2 | 1st Floor | 113 | Clean SPS | Demo
2 | 1st Floor | 112 | Operatory | Demo
2 | 1st Floor | 113 | Clean SPS | New
2 | 1st Floor | 112 | Operatory | New
2 | 2nd Floor | 210 | SPS | Demo
2 | 2nd Floor | C2W | Corridor | Demo
2 | 2nd Floor | 210 | SPS | New
2 | 2nd Floor | C2W | Corridor | New
2 | 2nd Floor | 255 | Pipe Chase | Demo
2 | 2nd Floor | 257 | SPS | Demo
2 | 2nd Floor | 259 | 2 Bed | New
2 | 2nd Floor | 257 | SPS | New
2 | 2nd Floor | 255 | Pipe Chase | New
2 | 2nd Floor | 254 | Toilet | New
2 | Attic | Attic | Attic Space | New
2 | Basement | 53 | Office | Piping
2 | 1st Floor | 109 | O.T. Clinic | Piping
2 | 1st Floor | Roof | Roof | Piping
2 | 2nd Floor | 210 | SPS | Piping
2 | 2nd Floor | 213A | Chase | Piping
2 | 2nd Floor | C2W | Corridor | Piping
2 | 2nd Floor | 235 | HAC | Piping
2 | 2nd Floor | Roof | 1st Floor Roof | Piping
2 | Attic | Attic | Attic Space | Piping
3 | 1st Floor | 113 | SPS | Demo
3 | 1st Floor | 112 | Operatory | Demo
3 | 1st Floor | 112 | Operatory | New
3 | Basement | 1 | Mechanical Room | Demo
3 | 1st Floor | 112 | Operatory | New
3 | 1st Floor | 112 | Operatory | Piping
3 | Basement | 1 | Mechanical Room | Piping
3 | Basement | 1 | Mechanical Room | New
28 | 2nd Floor | 210 | SPS | Demo
28 | 2nd Floor | C2W | Corridor | Demo
28 | 2nd Floor | 210 | SPS | New
28 | 2nd Floor | C2W | Corridor | New
28 | 2nd Floor | 255 | Pipe Chase | Demo
28 | 2nd Floor | 257 | SPS | Demo
28 | 2nd Floor | 259 | 2 Bed | New
28 | 2nd Floor | 257 | SPS | New
28 | 2nd Floor | 255 | Pipe Chase | New
28 | 2nd Floor | 254 | Toilet | New
28 | Attic | Attic | Attic Space | New
28 | Basement | 53 | Office | Piping
28 | 1st Floor | 109 | O.T. Clinic | Piping
28 | 1st Floor | Roof | Roof | Piping
28 | 2nd Floor | 210 | SPS | Piping
28 | 2nd Floor | 213A | Chase | Piping
28 | 2nd Floor | C2W | Corridor | Piping
28 | 2nd Floor | 235 | HAC | Piping
28 | 2nd Floor | Roof | Roof | Piping
28 | Attic | Attic | Attic Space | Piping
29 | 1st Floor | C02A | Low Voltage | Demo
29 | 1st Floor | 7 | SPS Storage | Demo
29 | 1st Floor | C01 | Hall | Demo
29 | 1st Floor | C02A | Low Voltage | New
29 | 1st Floor | 7 | SPS Storage | New
29 | 1st Floor | C01 | Hall | New
29 | 1st Floor | 7A | Office Fitting | New
29 | 1st Floor | C4 | Corridor | Demo
29 | 1st Floor | 146 | Clean/SPD | Demo
29 | 1st Floor | 148 | Patient Encounter | Demo
29 | 1st Floor | 150 | Patient Encounter | Demo
29 | 1st Floor | 145 | Waiting | Demo
29 | 1st Floor | 166 | Storage | Demo
29 | 1st Floor | 167 | Staff Lounge | Demo
29 | 1st Floor | C4 | Corridor | New
29 | 1st Floor | C5 | Corridor | New
29 | 1st Floor | 146 | Clean/SPD | New
29 | 1st Floor | 148 | Patient Encounter | New
29 | 1st Floor | 150 | Patient Encounter | New
29 | 1st Floor | 145 | Waiting | New
29 | 1st Floor | 166 | Storage | New
29 | 1st Floor | 167 | Staff Lounge | New
29 | Basement | C0WA | Soiled Utility | Demo
29 | Basement | 6C | Office | Demo
29 | Basement | C02A | Low Voltage | Demo
29 | Basement | 7 | SPD Storage | Demo
29 | Basement | C0WA | Corridor | Piping
29 | Basement | 7A | Office Fitting | Piping
29 | Basement | 6B | Clean Storage | Piping
29 | Basement | C02A | Corridor | Piping
29 | Basement | 7 | SPD Storage | Piping
29 | Basement | 11 | Stair | Piping
29 | Basement | 14 | MAS Storage | Piping
29 | Basement | 16 | HAC | Piping
29 | Basement |  | Mechanical Room | Piping
29 | 1st Floor | Roof | 1st Floor Roof | Piping
29 | 1st Floor | 148 | Patient Encounter | Piping
29 | 1st Floor | 167 | Staff Lounge | Piping
29 | 1st Floor | C5 | Corridor | Piping
49 | Basement | 14B | Office | New
49 | Basement | 14 | SPS | New
49 | Basement | 14A | Office | New
49 | Basement | 5 | Housekeeping Storage | New
49 | Basement | 2 | Mechanical Room | New
49 | Basement |  | Corridor | New
49 | 1st Floor | 130 | Clean Utility | Demo
49 | 1st Floor |  | Corridor | Demo
49 | 1st Floor | 130 | Clean Utility | New
49 | 1st Floor |  | Corridor | New
49 | 2nd Floor | 230 | Clean Utility | Demo
49 | 2nd Floor | 230 | Clean Utility | New
49 | 2nd Floor | 229 |  | New
49 | 2nd Floor | Attic | Attic Space | Demo
49 | 2nd Floor | Attic | Attic Space | New
49 | Basement |  | Corridor | Piping
49 | Basement | 6 | Mechanical Room | Piping
49 | Basement | C0C | Corridor | Piping
49 | Basement | 14B | Office | Piping
49 | Basement | 14 | Hall | Piping
49 | Basement | 14A | Office Space | Piping
49 | Basement | C0NE | Corridor | Piping
49 | 1st Floor | 130 | Clean Utility | Piping
49 | 2nd Floor | 230 | Clean Utility | Piping
49 | 2nd Floor |  | Corridor | Piping
49 | 2nd Floor | C2W | Corridor | Piping
49 | 2nd Floor | 206 | HAC | Piping
49 | Attic | Attic | Attic Space | Piping
50 | 2nd Floor | 229 | Storage | Demo
50 | 2nd Floor | 233 | Respiratory Therapy | Demo
50 | 2nd Floor | 229 | Storage | New
50 | 2nd Floor | 233 | Respiratory Therapy | New
50 | 2nd Floor | C2S | Corridor | New
50 | 2nd Floor | 291 | Clean Utility | Demo
50 | 2nd Floor | 290 | 2 Bed | Demo
50 | 2nd Floor | C2N | Corridor | Demo
50 | 2nd Floor | 291 | Clean Utility | New
50 | 2nd Floor | 290 | 2 Bed | New
50 | 2nd Floor | C2N | Corridor | New
50 | Attic | Attic | Attic Space | New
50 | Basement | 12 | HAC | Piping
50 | 1st Floor | 133A | Pipe Chase | Piping
50 | 1st Floor | 159 | Soiled Utility | Piping
50 | 2nd Floor | 233A | Pipe Chase | Piping
50 | 2nd Floor |  | Room, no # | Piping
50 | 2nd Floor | 259 | Soiled Utility | Piping
50 | 2nd Floor | 259 | Soiled Utility Pipe Chase | Piping
50 | Attic | Attic | Attic Space | Piping
51 | Basement | 17M | Staff Lounge | New
51 | Basement | 17 | Corridor | New
51 | Basement | 18 | Clean Linen Room | New
51 | Basement | 22 | Storage | New
51 | 1st Floor | 160 | Supply Storage | Demo
51 | 1st Floor | 162 | Soiled Utility | New
51 | 1st Floor | 160 | Supply Storage | New
51 | 1st Floor | C1W | Corridor | New
51 | 2nd Floor | 244 | SPD Supply | Demo
51 | 2nd Floor | C2E | Corridor | Demo
51 | 2nd Floor | 244 | SPD Supply | New
51 | 2nd Floor | C2E | Corridor | New
51 | Attic | Attic | Attic Space | New
51 | Foundation | F01 | Lower Mechanical | Piping
51 | Basement | 10A | Upper Service Room | Piping
51 | Basement | C0C | Corridor | Piping
51 | Basement | 14 | HAC | Piping
51 | Basement | 22 | Storage | Piping
51 | Basement | 18 | Soiled Linen | Piping
51 | 1st Floor | 129 | Locked Ward | Piping
51 | 2nd Floor | 240 | HSKPG | Piping
51 | 2nd Floor | 244 | Clean Utility | Piping
51 | 2nd Floor | 207 | Clean Linen | Piping
51 | Attic | Attic | Attic Space | Piping
111 | Crawl Space | Crawl Space | Crawl Space | New
111 | 1st Floor | 25 | SPS | Demo
111 | 1st Floor | 25 | SPS | New
111 | 1st Floor | 22 | Psych Office | New
111 | 1st Floor | 23 | Psych Office | New
111 | 1st Floor | CO-05 | Corridor | New
111 | 1st Floor | 24 | Clinic Office | New
111 | 1st Floor | 36 | Exam 4 | New
111 | 1st Floor | 25 | SPS | New
111 | 1st Floor | Crawl Space |  | Piping
111 | 1st Floor | Outside | Outside | Piping
111 | 1st Floor | C05 | Corridor | Piping
111 | 1st Floor | 25 | Clean Utility | Piping
111 | 1st Floor | 26 | Soiled Utility | Piping
111 | 1st Floor | 27 | Mechanical Room | Piping
116 | Crawl Space | 2 | Crawl Space
116 | 1st Floor | 128 | Assessment Consultation | Demo
116 | 1st Floor | 106 | Clean Utility | Demo
116 | 1st Floor | 26 | Soiled Utility | New
116 | 1st Floor | 128 | Assessment Consultation | New
116 | 1st Floor | 106 | Clean Utility | New
116 | 1st Floor | 142 | Corridor | New
116 | 1st Floor | 104 | Corridor | New
116 | Crawl Space | 2 | Crawl Space | Piping
116 | Crawl Space | 1 | Mechanical Room | Piping
116 | 1st Floor | 119 | Mechanical Room | Piping