## DesignConstruction Standards
St Cloud VA Design/Construction Standards Updated:11/25/19
DIVISION SECTION | Sub-Section | Basis of Design Notes | STATEMENT
Required Specification Sections (ALL Projects)
01-00-00, 01-32-16.15, 01-33-23, 01-35-26, 01-42-19, 01-45-00, 01-74-19, 01-81-13
Critical Common Specification Sections (Most Projects)
01-45-29, 01-45-35, 01-57-19,01-58-16, 01-91-00, 07-84-00, 07-92-00, 07-95-13,
DIVISION 01 | General Requirements
01 00 00 | 1.5E |  | Change 3m (10 feet) to 6m (20 feet) - Consult with NFPA 241
| 1.1D |  | Change VA retained testing company to Contractor retained testing company
| 1.4F |  | Parking permits are required. Contractor may park only in designated areas.
| Safety |  | Write ACE Safety Manual Section 21 into contract? More stringent fall protection. EM 385-1-1.
| 1.6H |  | Make sure specs and plans are clear about what type of construction fence must be used. 7 foot chain link construction fence required.
| 1.22F |  | Potable water may not be used for irrigation.
01 45 29
Infection Control Risk Assessment plan shall be designed/stated within specifications and construction plans, equal to the St Cloud VA standard.
Use NFPA Life Safety Code - Reference TIL.
Adhere to VA physical security requirements, reference the TIL.
Minors shall be designed to be LEED silver, project is not required to be certified via USGBC. A/e shall submit audit/report of completed project documenting their recommended USGBC LEED point level earned based on the USGBC point system. Report details shall be as equal to details required for USBGC reporting.
Indoor air quality management plan on all projects during construction, designed by the A/e. IAQ shall adhere to applicable ICRA, LEED, OSHA and EPA standards.
Design required construction testing to be completed by the contractor.
Unless the project takes care of this in 28 31 00, add the text in bold below in the appropriate section of 01 00 00 to insure that these modifications take place: The existing EST FireWorks graphic command center, located in Building 7, shall be modified to include graphical displays of the new or modified Building, using the FireWorks map view port capability. A graphical display of St. Cloud VA campus building layout shall be the default map viewport file. Additional map viewports for all levels of a remodeled or newly constructed building shall be programmed also. All alarm, supervisory and trouble device locations shall be mapped to both the campus building layout view and to the associated building floor plan on which the device is located.
A/e and applicable consultants shall perform applicable construction quality and compliance inspections per phase (underground, foundations, structural, framing, electrical rough-in, mechanical rough-in, plumbing-rough-in, building final). Inspections shall adhere to the Inspection Clause, shall include code review and written recommendations/findings submitted to the COR within 3 business days of the inspection.
Develop Interim life safety plan for all phases of work per NFPA that removes life safety systems from service during the project. Example, if fire protection systems are to be removed and relocated, A/e shall include designs for temporary protection/impacts during construction. "Means and Methods" by the contractor not allowed. It shall be designed and documented.
A/e shall receive the standard Division 1 general conditions from the COR. The A/e shall update the general conditions for the specific project. The COR and the A/e shall coordinate all details within Division 1 prior to finalizing the specifications.
All staging area, construction area and other fencing activities shall be at least 5' back from sidewalks and roadways.
All construction temporary fencing areas shall include at least (1) man gate with panic hardware to egress the construction site.
Show/Design All construction barriers, verify existing walls and doors are rated, if not replace/upgrade/ construct 1 hr temp barriers.
Create Submittal Schedule
All contracts with exterior impacts (including just a staging area, or driving, storing etc on turf area requires an errosion and sedimaent proction plan. Only high flow with opptional overflow dandybags shall be used.
DIVISION 02 | Existing Conditions
A/e and Construction contractors to use VA established benchmarks for elevations.
02 41 00 |  |  | Construction barriers to be non-combustible 1 Hr. minimum construction barrier, or equal to adjacent permanent barrier, whichever is more stringent.
ICRA to be implemented. Consult with ICRA team and permit.
Inspect all existing conditions within the project bounds of construction and areas impacted by construction. Use government as built for reference only. The design shall be coordinated with existing conditions, as built documents and the design contract.
The A/e team shall document all existing equipment and the equipment's EE number to be removed or relocated under the design. The EE number is listed on equipment via a white sticker with black lettering. The equipment and EE number shall be listed in spreadsheet format and submitted to the COR prior to entering the construction document phase.
A/e shall photo document existing conditions during their field investigation. Photo documentation shall be subject to VA policy, coordinated with the COR. Photos shall be submitted to the COR on compact disk upon completion of the field investigation. A minimum of 50 photos shall be taken documenting the overall site impacted by construction. The intent is to document the preconstruction site condition prior to the completion of the design.
DIVISION 03 | Concrete
03 30 00 | 1.3 |  | Contractor retained testing company
Primary structural components shall be concrete structures only (cast in place or pre-cast). See division 5 for additional details.
6” sidewalks with rebar, 6' minimum width unless otherwise approved.
Attic and unoccupied areas shall be separated from below floors and occupied areas by concrete floors.
| Part 2.2.Q |  | Supports, Spacers, and Chairs: Will be plastic within cast in place concrete.
Aesthetic precast components shall match adjacent buildings.
DIVISION 04 | Masonry
04 20 00 |  | ACME Brick | OCHS Harvard blend basis of design unless otherwise noted or required by SHPO. A/E To perform Market Research to identify an acceptable product. Harbard Blend is out of production.
Brick Masonry exterior to match adjacent building/structure, vendor and color mix to be coordinated with VA and SHPO.
Pre-cast masonry panels to match adjacent building or as directed otherwise.
DIVISION 05 | Metals
ALL secondary steel members used such as masonry lintels shall be fire protected by sheetrock assemblies, no spray fire proofing or other methods allowed. Structural Steel components shall never be used as primary structural components, unless written approval is granted by Chief Engineer (i.e. remodeling situations).
|  | Bollard for Auto Door Operator switch | Suggested text for drawing or SPEC: provide a bollard for exterior handicap push pad, bollard shall be dark bronze anodized aluminum 6" X 6" X 42" tall surface mount. Basis of design: WIKK Accessibility BPS SM PRP26 DB or equal.
No wood backer or substructure allowed within building envelope, steel only.
All exterior hand rails shall be stainless steel.
Patient Lift structural support shall be designed and included in the construction contract.
DIVISION 06 | Wood and Plastic
06 10 00 |  |  | No use of wood anywhere inside the building envelope, i.e. backing, blocking, furring, etc. except wood door slabs and MDF casework. Backing shall still be metal. Any variation in design requires written approval by the Chief Engineer.
Any approved wood (exterior sheathing, roof blocking etc.) shall be certified by Forest Stewardship Council (FSC). This includes wood doors.
DIVISION 07 | Therm and Moisture
07 21 13 |  |  | Interior of Building Envelope Insulation: Mineral wool of 70% recycled content for all non LEED projects or 75% recycled content for all LEED projects. No other product types allowed. Including plumbing insulation. "NO glass fiber", nor "fiber glass" insulation allowed. NO formaldehyde products allowed.
No spray foam insulation shall be used.
07 84 00 |  |  | Only red fire caulk allowed. No other color of fire caulk permitted. Require 3rd party fire proofing and caulking inspections. Use 25% sampling method with a 10% retest requirement until all samples pass.
07 31 13 |  |  | Asphalt Shingles to be 3 tab, 30 year warranty, match existing/adjacent structure.
07 60 00 |  |  | All flashing and sheet metal shall match adjacent structure unless approved in writing otherwise. Campus typical is dark bronze. Profile of flashing is subject to SHPO standards and historic profiles previously approved on campus.
No spray applied products.
07 92 00 |  |  | All non fire caulking products shall be a color other than red.
DIVISION 08 | Doors and Windows
Fire doors to be metal doors.
Any written exceptions to allow wood fire doors shall be designed without armor plates nor kickplates. All door hardware accessories shall be rated to match the barrier assembly rating.
08 11 13 |  |  | Hinge and Latch locations to match Steel Craft
08 11 13 |  | 2.7.I.3. | As a general rule, "terminated stops" or "hospital stops" are preferred in all areas (not on exterior doors). Verify with COR and Integrated Project Team what is preferred on specific projects.
Mortised latches
ALL hollow metal door frames shall be filled with grout.
Knock Down frames not allowed, fully welded frames with "face welds" required.
"Jambless" frames shall only be installed where required by VA, such as within controlled Mental Health spaces.
08 17 10 |  |  | Dutch doors not allowed
Wood doors to meet FSC Requirements. Reinforced for hardware - closers
08 71 00 |  |  | Use Corbin or Best Mortise locks. Use Best cylinders 7-pin TE keyway
Corbin ML2000 SERIES- ML2055 Classroom, ML2057 Storeroom,
ML2069 Patient Bathroom, ML2065 Dormitory (Deadbolt Feature)
Use Mortise locks only, no cylindrical locks
Prefer electric strike located in door frame. Discourage use of electric mortise inside doors - maintenance issues with wiring failures when routing through hinge and door. No wires shall run through door hinges and door slabs.
All double doors shall be spec'd with "Z" shape, metal astragal and door coordinator
08 71 00 | 2.9 |  | CORE shall be removable with special tool or key
|  | Detex | ECL-230D
|  | Closer | Corbin Russwin DC6210
|  | Exit device push bar | Von Duprin #98/99 series
|  | Hinges | Hager BB1279 4.5" x 4.5" 5 knuckle ball bearing US 26 D HT
|  | Card Reader | Best Basis 6 45HG7DV3MS626 RHTRK3
|  | Electric Strikes | Folger Adam 12/24v failsafe
Public restrooms shall have occupied latch identification.
A specific DETAILED hardware coordination meeting is required between the A/E's hardware expert and the VA's hardware expert prior to completion of the design.
Access panels shall be finished painted to match the adjacent surface. All access panels required for maintenance and continued service shall be shown on the construction documents. Designer shall coordinated with design disciplines to determine locations and quantities.
White birch doors interior wood doors to match existing. No other products allowed without written approval.
Window alterations, additions and deletions are subject to SHPO comments. All windows shall match historic profiles and comply with VA physical security manual unless approved otherwise in writing.
No aluminum store front assemblies within the building envelope. Exterior store fronts shall be dark bronze.
No glass below 18" AFF.
No wire conductors within hinge assemblies. All wire conductors for door hardware shall be on the latch side with latch activation. Electronic plungers not allowed.
All exterior doors, windows, flashing, and other coordinated finishes shall be dark bronze.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 09 | Finishes
09 29 00 | Gypsum Assemblies |  | All penetrations in any wall, floor, or ceiling/substructure shall be sealed with appropriately rated sealant (consider fire/smoke barrier ratings). All walls shall be designed from floor to floor (including insulation) unless the wall is specifically designed as a "knee wall".
No laminating (gluing) of sheetrock to surfaces. Metal vertical framing substrate shall be used.
09 30 13 |  |  | Do not use white grout - Off white is acceptable when appropriate.
09 30 13 | 2.6D |  | Do not spec any unsanded grout. Make joints 1/8 inch and wider.
09 51 00 | ACT/Ceiling Assembly |  | Match existing ACT system unless specialty system is specifically required by SOW or VA design criteria. Written approval required prior to designing a specialty system. Coordinate gypsum ceilings in "wet" areas as coordinated in writing with the VA. Ceiling heights shall comply with VA design guide. Unless otherwise noted within the design criteria a minimum of 9' is required. When 9' is not achievable, written approval is required from the VA prior to proceeding. Gypsum soffits shall be used with prior approval from the VA to coordinate ACT ceiling assembly heights and MEP systems designed above the ceiling assembly.
| Ceiling Grid |  | USG Donn DX
| Ceiling Tile |  | USG 2110 2' x 2' Match existing ACT tile.
09 65 13 | Resilient Base | VPI brand | Colors: 56 Patriot, 59 plum, 89 ivy, 14 taupe, Fawn vinyl base is campus typical.
vinyl, roll, 1/8' thick, cove toe, height per SOW or drawings
09 65 19 | floor tile | Armstrong | Fortress White # 51839 - Campus typical
Camel Beige # 51805
Dutch Delft # 51916
Teal # 51906
Smokey Brown # 51868
VCT flooring design shall reflect campus typical. Accent colors shall be used as border accents unless directed otherwise. Hallways shall have fortress white as the main tile with Smokey Brown as the border tile.
| VCT |  | VCT shall be quarter turned in rooms and in the direction of travel in corridors.
| Rubber | Johnsonite | HRTSP 543 1/8" 24" Tan Spec
|  | Johnsonite | 12" x 12" Prima EF4 12" B721EF-4012 Cream/Brown
|  | Marley Flexico | 12" x 12" LR-75 1277 RN-018 Light Green
09 91 00 | paint |  | Primer coat to be white in color.
|  | Benjamin Moore | Eco Spec: white #962 standard wall
Eco Spec: Smokey Mountain # AC-18
Eco Spec: Evening Dove # 2128-30
Eco Spec: Shaker Beige # HC-45
Eco Spec: Cabernet # 2116-30
Bronze Tone P25 60-low luster Maintenance Coating, Windows and Doors, Super Spec
Moorlife Flat Exterior Acrylic House Paint (N105) Tinted to VA Thorosheen Grey Ext.
SPRAY APPLICATION NOT ALLOWED of any product
09 94 19 |  |  | No Wall Covering Allowed other than paint unless specifically approved in writing.
Access panels shall be finished painted to match the adjacent surface. All access panels required for maintenance and continued service shall be shown on the construction documents. Designer shall coordinated with design disciplines to determine locations.
Acrovyn handrails with quick disconnect system to match existing. Reference VA submittal. No other systems allowed unless specifically approved in writing.
Vinyl base to match campus typical.
Attic Stock: 10% of total installed material quantity shall be turned over to VA for attic stock. Attic stock shall be new and unused material. Attic Stock material is required for VCT, ACT (tile), Ceramic Tile, Specialty Coatings, Specialty Coverings and any other uncommon finished. A/e to edit specifications to include the verbiage.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 10 | Specialties
10 |  |  | All items within division 10 appropriate for the project shall be included within the design and included in the construction budget.
10 26 00 | Hand Rail | Acrovyn | HRB-4CN color #100 eggshell
|  | Acrovyn | HRB-4CCMHLN(Ligature resistant) to be used in Locked ward areas and as required. Color #100 Eggshell
|  | Acrovyn | Quick lock mounting system for hand rails
| Corner Guard | Acrovyn | SSM-25AN color #100 Eggshell
| Door Guard | Acrovyn | Acrovyn 4000 .060" kick plates Color #209 Slate
| Crash rails | Acrovyn | SCR-48N color #100 Eggshell
Coordinate toilet, bath and laundry accessories with the VA typical products.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 11 | Equipment
Some Division 11 items are funded separately from the construction budget via a VA Activations (FFE) source. Consult the decision tree. A/e shall include design coordination time to ensure space, utilities and all equipment requirements are designed into the project to support fully functional equipment. If the VA does not have an equipment vendor on contract, the A/e shall coordinate with the VA to determine a basis of design for the equipment.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
| Patient Lifts |  | Patient Lifts - Structural support is via the construction contract. The equipment track and lift module is via the VA's equipment process. The designer shall design an "H" track system for 100% coverage of the required room. https://www.publichealth.va.gov/docs/employeehealth/Pt_Hdlg_Design_Equip_Coverage_Space_Recs.pdf#
DIVISION 12 | Furnishing
12 31 00 |  |  | Items required for the project under this specification shall be included in the design and construction budget.
12 32 00 |  |  | Items required for the project under this specification shall be included in the design and construction budget.
12 34 00 |  |  | Items required for the project under this specification shall be included in the design and construction budget.
12 36 00 |  |  | Items required for the project under this specification shall be included in the design and construction budget.
Other items required under other specification sections of division 12 shall be funded by VA Activation (FFE).
Millwork Systems with a key core: the keyed system shall be Best 7 pin.
Modular Furniture Systems shall be customized to a keyed Best 7 pin system.
All Lockers shall accept the VA lock standard, no hasp locks.
DIVISION 13 | Special Construction
All items within these specification sections shall be designed and funded via the construction budget.
DIVISION 14 | Conveying Equipment
Strip lighting the whole length of the shaft - switched at each floor
Controls System should have an integral Time clock that would allow the user to define the hours of the day that the cab is in operation.
Stainless steel cab
Rubber flooring
Rails to shield the buttons to prevent accidental activation
A fire-suppression sprinkler in the pit and a heat detector located at the top of the hoist way
Provide brackets/fixtures/pipe/etc. for a support leg to be utilized beneath the cab for lock out/tagout potential energy isolation. Fixtures to be attached to cab frame and to support steel on the pit floor.
Hoist way must have adequate head clearance per code
Minimum clear length of 96" and a preferred width at the floor of 69" cab dimensions
National code now requires elevators to have a surveillance camera in the elevator cabs. Minnesota code does not currently recognize this. SCVA electric shop would prefer we follow the new national code.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
Elevator Systems/equip/devices with a key core: the keyed system shall be Best 7 pin.
Elevator Work shall have an independent special inspection funded by the General contractor. Inspection to be by a third party qualified elevator inspector. Include this requirement within the special testing specs and the elevator specs.
DIVISION 21 | Fire Suppression
21 05 11 |  |  | Grooved, compression and mechanical Fittings Not Allowed. Threaded fittings only.
Johnson Controls for building automation system
Edwards fire protection panels
St. Cloud Fire Department specifies a 5” Storz type (sexless) FDC connection for the exterior of buildings that incorporates a debris screen.
Fire sprinkler design shall be thoroughly detailed with the design documents. Including coordination with MEP design to ensure sufficient ceiling space for clearance to all adjacent MEP systems for future maintenance. It is the A/e's responsibility to coordinate their basis of design for constructability.
A/e shall test water pressure for completion of their fire protection design.
Sprinkler heads shall be centered within the ACT tile.
A/e shall design temporary system for remodels when the existing system is to be removed and reinstalled. It is the A/es responsibility to clearly design a temporary method/system to comply with Joint Commission, NFPA and VA requirements.
Main fire suppression service to be connected to the domestic water main service. Upon entering the building's heated environment, the services shall be separated.
Zones and isolation abilities shall be designed in a manner to favor maintenance and minimize patient/staff impacts upon needed maintenance work.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 22 | Plumbing
Bypass valve to be Globe type.
Cut off valves to be Gate type.
pressure gauge to be installed down stream of bypass and gate valve when present.
22 05 11 |  |  | Grooved, compression, and mechanical Fittings Not Allowed. Only threaded, welded or soldered connections allowed.
Always use Dielectric fittings between dissimilar metals
Install clean-out at each lavatory. Clean-out to be above spill line of lav. Install clean-out behind mirror if present.
No PVC pipe allowed within the building envelope, exterior buried situations only.
22 05 11 | 3.1B |  | Clearly call out accessible items (VAV boxes, J-boxes, valves). Specs may say unrealistic access (from floor and 3' clear). Consult manufacturers requirements and coordinate with VA staff for clearances. The A/e shall design maintenance clearances within the design documents to ensure proper clearance for future maintenance.
22 05 23 |  |  | Valves: < 2"= ball, >2"= Butterfly Lockable if applicable
Access panels shall be finished painted to match the adjacent surface. Reference previous access panel note.
Design zoning valves to isolate systems (i.e. steam/hot water convectors) within 1 room for maintenances purposes.
| PRV | Spence | Consult with COR and VA plumbing shop for specific design of campus typical PRV system.
22 40 00 |  |  | All fixtures to match existing campus standard unless otherwise specifically approved in writing. Wrist blade, tall gooseneck. No areators. No senor faucets.
22 40 00 |  |  | Toilets to be wall mounted. Bariatric rated and reinforced.
22 40 00 | Sink Support |  | Sink carriers/supports shall have reinforcement feet installed to ensure flexing does not occur.
| Medical Gas Systems |  | Order of medical gas outlets shall be Oxygen, Air, Vacuum (OAV).
Distribution lines shall be parallel and perpendicular to building grid lines. No angled lines shall be accepted in construction.
22 40 00.2.11 |  | ELKAY EZH2O | Install water cooler with bottle filler option in new construction
Plumbing lines requiring a closed cell insulation shall be coordinated for basis of design with the plumbing shop.
22 13 00 |  |  | Minimum diameter of waste vent and drain piping is to be 2"
No wet tapping devices allowed, i.e. saddles
Zones and isolation abilities shall be designed in a manner to favor maintenance and minimize patient/staff impacts upon needed maintenance work. Zone and isolation shutoff valves shall be designed in an abundance. They shall be illustrated on the plans. Wings or similar large sections of buildings/floors shall not be considered a zone. Each device/equipment/fixture shall have isolation valves. Include domestic water balancing requirements for the construction constructor. Include a requirement for a balancing report.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 23 | HVAC
23 05 11 |  |  | Grooved, compression, and mechanical Fittings Not Allowed. Welded, soldered or threaded connections only. Exception - HVAC duct work shall be slip joint or fastened connections.
Always use Dielectric fittings between dissimilar metals
|  | Spirotherm | Spriovent Filter/ Air separator preferred
Always Spec Grounding kit with VFD's
23 05 11 | 2.3H |  | After TAB final, belts and sheaves shall be listed with size and quality label
23 05 11 | 2.14A |  | Replace A with 'contractor to furnish and turn over to the COR tools not readily available commercially that are required for assembly, disassembly, set-up, commissioning, testing or adjustment of equipment furnished.'
23 05 11 | 3.1B |  | Clearly call out accessible items (VAV boxes, J-boxes, valves). Specs may say unrealistic access (from floor and 3' clear). Illustrate maintenance clearances within the design documents to keep manufacturer recommended clearances. Designers shall be responsible to coordinate the design details and basis of design products to comply with maintenance clearances.
23 05 41 | 3.1 |  | Add paragraph 'Isolators shall not be mounted to roof, columns, trusses or any other building structure without prior approval of the COR.
23 05 93 | 3.6C |  | Change 20% to 10%
23 07 11 | 3.?. COMMISSIONING |  | Add to Paragraph A. "If checklist is not provided to the COR prior to commissioning and approved by the COR, all work will be null and void and shall be redone."
23 05 23 |  |  | Valves: < 2"= ball, >2"= Butterfly Lockable if applicable
Install zoning valves for systems (i.e. steam/hot water convectors) for maintenance isolation to isolate individual rooms.
23 10 00 |  |  | Underground Fuel Tanks shall be Fiberglass Reinforced Plastic Tanks
| 23 21 13 | Axiom SF100 | Glycol makeup system tank and pump equipment
23 21 13 |  | Koil Pak / Nexus | Pre-piped Hydronic Manifolds, Valves and controls
23 21 13 | 3.5.A.4 |  | Re-fill system as needed until all air has been purged from the system.
23 25 00 | 3.1G or H
23 31 00 |  |  | No internally insulated duct
No 'egg crate' or perforated diffusers or grills
No turning vanes in outside air intake, exhaust or return air ductwork systems. Turning vanes not allowed in any unfiltered air stream.
Maximum length of flex duct is 4'-0". Flex duct to be used to attach to diffusers and return grilles only.
All HVAC requirements for testing are to meet 0 to + 10%
No more than 4% HVAC system loss allowed
23 31 00 | 2.3A.1
23 31 00 | 3.2C |  | Remove 4% leakage requirement. Add "The maximum leakage rate allowed shall be calculated based on duct leakage class, square footage of the duct segment tested, and static pressure applied during the leakage test."
23 31 00 | 3.1D |  | Fire/smoke dampers must be exercised before operation of HVAC system and after all duct work and adjacent systems/assemblies are installed. During final inspection the contractor shall operate
23 36 00 |  | HVAC Manufacturing | VAV Ready Unit (VRU) Johnson Controls Model (Basis of Design)
23 36 00 | 2.2D.2 |  | Provide duct access panels on both sides of coils. Design details of clearances required to operate, inspect and service dampers on annual basis.
23 40 00 | 3.2 |  | Contractor to maintain all filters (on 3 month intervals) until the project is completed. Provide the VA with 1 spare set of filters at the completion of the project. This spare set shall be separate of and in addition to any previous set used for the contractors use during and after completion of construction.
Access panels shall be finished painted to match the adjacent surface, reference previous access panel note.
Perforated diffusers are not allowed (except suicide prevention models when used in locked psych ward)
Johnson Controls for building automation system
AHU shall be inside the buildings, not roof top units. Designer shall coordinate basis of design with all design disciplines to ensure proper maintenance clearances are coordinated and documented within the construction documents.
Design 100% redundant perimeter steam or hot water convector heating system in addition to overhead systems. Parallel distribution system shall be used to reduce impact to adjacent spaces during maintenance and repairs.
Ducted HVAC returns only, no plenum systems/returns allowed.
No egg crate return grilles allowed.
VAV HVAC system only; unless the design guide specifically requires only a different system. In this scenario obtain direction in writing prior to proceeding.
New heat pump systems shall be designed similar to the B116 system. Dedicated Buffer tanks with dedicated primary pumps for the heat pumps system.
AHU Heating Coils be heated by 40% water/ propylene glycol system, not steam. New convectors on exterior walls are to be heated by hot water, not steam.
Distribution lines shall be parallel and perpendicular to building grid lines. No angled lines shall be accepted in construction.
VAV valves and controls shall be on the same side, within arms reach off a ladder. VAVs shall be of the style and brand that come factory direct assembled with valves, controls ands coils preassembled on the same side for access and maintenance.
Zones and isolation abilities shall be designed in a manner to favor maintenance and minimize patient/staff impacts upon needed maintenance work. Zone and isolation shutoff valves shall be designed in an abundance. They shall be illustrated on the plans. Wings or similar large sections of buildings/floors shall not be considered a zone. Each device/equipment/fixture shall have isolation valves.
Electric Reheat units Shall NOT be used. Electric power heating units shall not be used. Hot water or steam powered only.
TABs shall occur for Air and Hydronic systems. They shall occur for all phases (temporary and/or permanent) and at completion of the project.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
St. Cloud VA prefers that the humidifier coils be an integral component of the AHU rather than duct-mounted
Fire dampers shall not be installed in walls. They shall be installed in floors; unless approved in writing (specifcally approved from the Chief Engineer).
|  | HVAC Filters & Filter Banks | Filter Bank tolerance requirements require inmprovements and custom tolerances. Coorindate with M/O supervisor for specific details.
HVAC Systems/equip/devices with a key core: the keyed system shall be Best 7 pin.
Do not place units under the roofline, risk of falling ice/snow damages exterior units.
DIVISION 25 | Integrated Automation
Johnson Controls for building automation system
DIVISION 26 | Electrical
26 05 11 |  |  | Panels are to have labeling for all circuits and identify where its fed from
Emergency receptacle wall plates are to be stainless steel with clear labels and black letters designating the panel and circuit number feeding the receptacle.
All wall plates for lighting switches and branch circuit receptacles are to be labeled with the panel and branch circuit supplying the device.
26 05 11 | 1.9 C3 |  | Work on energized circuits…written approval obtained from the Health Care System Director through the Facilities Management Service Line Director and the COR
26 05 11 | 1.9F |  | ….trades to minimize interference and meet code required clearances
26 05 11 | 1.10 |  | Clearly call out accessible items (VAV boxes, J-boxes, valves). Specs may say unrealistic access (from floor and 3' clear). Maintenance clearances shall meet manufactures requirements and coordinated with the VA.
26 05 11 | 1.11B |  | remove screws… add secure nameplates with bolts or rivets.
26 05 19 | 2.1 C5 |  | replace (e.g., pink and purple) with (pink=switch leg, purple= traveling wire)
26 05 19 | 3.1H |  | delete 'Use expanding foam or'
26 05 19 | 3.8C |  | add Rotation tests to be witnessed by the VA
26 05 33 |  |  | No conduit less than 3/4 " allowed. (with the exception of 1/2" dia. whips)
No flex conduit. Use whips for lighting only (max 4')
No compression fittings
Minimum size for all ceiling boxes for branch circuits is 4-11/16” x 2- 1/8” deep.
26 05 33 | 3.2D |  | A maximum of 360 degrees of bends may be used between any junction box or pull box
26 05 33 | 3.5C |  | remove 'Conduit shall be half-lapped with 10 mil PVC tape before installation. After installation, completely recoat or retake any damaged areas of coating.'
26 05 41 |  |  | Depth for medium voltage concrete encased duct bank is 3 feet to top of envelope.
26 24 16 |  |  | All electric equipment, (i.e. main distribution boards, switchboards, panel boards, disconnect switches,) need to be labeled with the source of power they are fed from and the equipment/ devices served.
Panel schedules are to be updated when adding or removing circuits.
26 24 16 | 3.1B |  | add ' If in a finished wall, stub up additional conduits for future use, coordinate with COR.
26 29 21 |  |  | Breakers 200 amps and greater to have test port for secondary injection testing.
26 36 23 |  |  | Transfer switches to have annunciator/ control panel installed in the generator shack that provides the source of power to them, and be connected for remote transfer control.
|  | Generators | Incorporate into spec: 1 second start, 30 minute EM to Normal, 5 minute cool down
26 51 00 |  |  | Lenses of lighting fixtures to be sealed/ gasketed to prevent bugs from entering the lens.
26 56 00 |  |  | Incorporate into spec: Photocell control for exterior lighting
Access panels shall be finished painted to match the adjacent surface. Designer shall design quantity and location of access panels per the basis of their design.
Dead front transformers only.
Copper wire only. Aluminum not allowed.
¾” electrical conduit is the smallest conduit to use on a project.
Show all equipment code/manufacturer clearances on the plans (VAVs, electrical panels, etc.)
Design medium voltage switches with basement cavity. Basement cavity "floor" to be rock.
Medium voltage loop shall be concrete encased
Use LED interior lights
Dimming systems for LEDs will be 0-10 volt control
Johnson Controls for building automation system
Distribution pathways shall be parallel and perpendicular to building grid lines. No angled lines shall be accepted in construction.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
Electrical equip/devices with a key core: the keyed system shall be Best 7 pin.
DIVISION 27 | Communications
27 | Cable and Conduit |  | All cat cable shall be VA EHRM compliant per current OI&T publications. All cat 6 or newer cable shall be installed in 1" or large blue conduit.
| Public Address and Mass Communications |  | 70 Volt speakers with Bldg. amplifiers in each Bldg. (We will be using the Lowell Dual Coil Speakers from the EST3X Fire Alarm system for PA announcements where already installed.) Unknown what Brand of system we will get for the PA Head end.
27 52 23 | Nurse Call & Code Blue | Borg Rauland | R5000 System (Sole Source) as this must interface with current system
27 52 23 | Audio station w/staff assist | Borg Rauland | R4K14SA
27 52 23 | Code Blue | Borg Rauland | R4KCB13
27 52 23 | Dome light | Borg Rauland | CLA-244
| Patient Wandering System | Secure Care | SC-40 System with 40 GHZ frequency (Sole Source)
Ademco panic alarm systems.
Consult with COR and IT, Biomed and Bio electric for current requirement information
Distribution pathways shall be parallel and perpendicular to building grid lines. No angled lines shall be accepted in construction.
Any Special Tools required for maintenance and/or operation of basis of design and installed product shall be included within the specifications.
DIVISION 28 | Elec Safety and Security
| Fire Detection and Alarm | Edwards Signal Technology | EST3X panels & Devices (Sole Source)
28 31 00 | Fire Detection and Alarm | Fireworks | Add text to this Chapter and to the General Requirements as follows: The existing EST FireWorks graphic command center, located in Building 7, shall be modified to include graphical displays of the new or modified Building, using the FireWorks map view port capability. A graphical display of St. Cloud VA campus building layout shall be the default map viewport file. Additional map viewports for all levels of a remodeled or newly constructed building shall be programmed also. All alarm, supervisory and trouble device locations shall be mapped to both the campus building layout view and to the associated building floor plan on which the device is located.
| Security Detection | Ademco | Must be compatible with out Ademco 685 Receiver @ the Monitoring station
| Video Surveillance | American Dynamics | Intelex system with DVD/CD burner and at least a 500GB hard drive
| Physical Access Control Systems | UTC | M2000 Controller 4/2 door with Wiegand WIU-4 for each door controlled
| (CONT) | Schlage | MT15-485 PIV readers for Low/Med Security doors; MTK15-486 PIV readers for High Security Doors
Access panels shall be finished painted to match the adjacent surface, reference previous statement regarding access panels.
Johnson Controls for building automation system
Distribution pathways shall be parallel and perpendicular to building grid lines. No angled lines shall be accepted in construction.
Communication Systems/equip/devices with a key core: the keyed system shall be Best 7 pin.
DIVISION 31 | Earthwork
Fuel tank bedding shall be 12” pea gravel not sand
Design erosion control/SWPPP plan for project, campus is an MS4 entity. All impacts of this project shall be addressed by the designer of record. Including the staging/parking area impacts.
Adhere to Sauk River Water shed when project requires a permit.
SOD will be used to repair grounds. Seeding will not be allowed.
DIVISION 32 | Exterior Improvements
32 90 00 | 1.6B |  | Add minimum 5 years landscaping as their primary profession.
32 92 00 |  |  | Add minimum 5 years landscaping as their primary profession.
1 1/2" Bryan Red Rock for landscaping rock shall be used
Sod to be used for landscaping grass areas, Seed as deduct option only
Simplistic landscaping shall be designed unless otherwise noted.
Seed to be "Landscaper's mix" as sourced from Central Landscape Supply, or approved equal.
Sod to match "Landscaper's mix" seed blend, or approved equal.
All temp sidewalks shall be concrete/concrete slurry/asphalt hardscape. No gravel. All temp sidewalks shall be illuminated and slope ADA slope compliant.
DIVISION 33 | Utilities
Fiberglass underground fuel tanks, not steel
Fuel tank bedding shall be 12” pea gravel not sand
|  | StormTech | Storm tech underground infiltration systems are currently used on campus.
DIVISION 34 | Transportation
DIVISION 48 | Elec Power Generation
St Cloud VA Design/Construction Misc. Items
RFI’s shall be reviewed, answered and returned within 10 business days by the A/e
Estimates by the A/e for change order work by contractor to be provided to VA within 5 business days of the VA request.
Submittals shall be reviewed by the A/e, comments provided and returned within 10 business days. VA will send hardcopy plans to A/e, not electronic submittal exchange.
ASI/PR shall be issued by A/e within 15 business of the discovery of the need.
A/e Design period submittals delivered to VA at minimum 10 business days prior to meeting.
A/e shall call into each construction progress meeting (biweekly throughout duration of project).
Identify equipment EE’s numbers for equipment that is to be removed and replaced during construction. Submit a list of EE numbers to COR after the field inspection is complete prior to entering the "construction document" phase.
Include code black criteria in the design (i.e. single source exterior lock down of the area). Switch shall be located in secure, quickly accessible area.
Include compact disk of all documents with each design submission in pdf and AutoCAD formats.
Also Include (1) 11X17 copy of final plans at time of construction award including all addenda’s.
Anticipate SHPO consulting for all exterior modifications, new buildings, additions. A/e to draft initial intent SHPO memo to VA (prior to schematic design, a schematic design SHPO submittal, a 30% CD SHPO submittal, a 50% CD SHPO submittal and a 95% CD SHPO submittal. Each review by SHPO takes a minimum of 30 days for response by SHPO. A/e shall include SHPO review process into their design and schedule.
A/e shall coordinate the design disciplines specific space requirements to ensure sufficient space within the existing and new cavities for all equipment and utilities. A/e shall show specific coordinate details for contractor to adhere to during installation. The A/e shall field verify and coordinate all aspects of their design to ensure constructability.
Construction materials shall be ASTM Class A.
No blue tooth or other wireless connected technology that could be used to transmit PHI or PII will be allowed. No basis of design products shall be proprietary in nature, unless approved in writing from the Chief Engineer. Any special tools required for maintaining equipment (tools/programs/devices) shall be provided by the contractor as part of the contract. The A/e team shall research the products and provide specific details.
The A/e shall research all products, pathways, clearances, and other aspects regarding installation of assemblies for construction implementation. The drawings shall be accurate for a contractor to install the basis of design material/products in the identified locations.
The design of the project shall conform to the style of the campus. The final product shall "fit in" with our existing style interior and exterior. The goal is to make the product look as though it has always been here. Reference TIL design alert 147 -"Foundation of Design"
Should the St Cloud VA Design/Construction Standard conflict with the design standards published on the TIL, VA national criteria, code or other regulatory published data the A/e shall notify the COR, make a recommendation on which to adhere to and receive written direction by the chief engineer on which standards apply.
A/e shall reference PG-18-1, PG-18-3, PG18-4, PG18-5, H18-8, PG-18-9, PG-18-10, PG18-12, PG 18-13, PG 18-14, PG 18-15, PG 18-17, D-7545, H7545, and the other related design criteria published on the TIL.
Special Instructions - Directives
VHA Publications |  |  | https://www.va.gov/vhapublications/publications.cfm?Pub=1
1002.1 |  | NRM Program
1028 |  | Facility Electrical Power Systems
7715 |  | Safety and Health during Construction
7712 |  | Fire Protection Code Reviews of Delegated Construction Projects
7707 |  | GEMS
7704 (1) |  | Eyewash
MH 1167 |  | MH EOC Checklist
1108.07(1) | Loris Schofield | Pharmacy General Requirements
1116(2) |  | Sterile Processing Service
1761 | Shawn Ogelsby | SUPPLY CHAIN MANAGEMENT OPERATIONS
1037 |  | RANDOLPH-SHEPPARD ACT COMPLIANCE
Patient Privacy Directive | TIL
Security Directive | Tim Foss | 730
OIT
EHRM
Safe Patient Handeling

## Pictures of Standards
Standard Lavatory Assembly
Faucet
Urinal Assembly
Toilet Flushometer
Toilet Grab Bars & Toilet Paper